## Instructions
Strata Electrical Planning Report Guide Template (Draft)
Instructions
Updated May 2026
General Notes
1. If desired, copy and paste directly from the SEPR workbook to support the electrical planning report.
2. For more information, refer to the guidance.
Section 1 - Property and Company Details
1. Date and Property Details
a. Enter the date of the electrical planning report.
b. Confirm if each strata lot is supplied with power independently from each other strata lot
i) If yes, only Section 1 is required for the electrical planning report plus a statement saying that the strata lots are supplied with electricity from the utility independently from each other strata lot. A description of the electrical distribution to support the statement should be included.
c. Enter site information and strata number.
2. Site or Building Contact
a. Enter details and contact information of strata representative or site contact.
3. EPR Provider Contact and Qualifications
a. Enter details and contact information of the person who is completing the electrical planning report.
i) The person completing the electrical planning report must be an electrical professional engineer, a registered applied science technologist, or a journey person as defined in the regulation.
4. Error and Omission Insurance
a. If applicable, attach a copy of Error and Omission Insurance at the end of the electrical planning report.
Section 2 - Executive Summary
1. Introduction
a. Provide a short introduction describing the purpose of the EPR. Refer to the guidance and template for more information.
2. Summary
a. Provide a summary highlighting the most useful information, to the strata corporation, contained within the EPR. Refer to the guidance and template for more information.
Section 3 - Electrical System Details
1. Existing Electrical Service Capacity
a. Conduct a site visit to confirm the ratings and operating voltage of the service entrance equipment.
b. Determine the current peak demand on the service using one of the following methods:
i) Hourly (kWh) demand data from the utility with application of safety factor to allow for variation in peak demand (kW).
ii) Adding up the connected loads on the service.
iii) Any other method determined by the EPR provider.
c. Enter the method that was used for the peak demand calculation.
d. Enter the estimated remaining service capacity by subtracting the peak demand from the electrical service capacity.
2. Existing Electrical Demands
a. This includes any major electrical loads such as:
i) Heating, cooling, and ventilation systems.
ii) Electric vehicle charging infrastructure.
iii) Lighting and plug loads.
iv) Elevators.
v) Large motors.
b. Identify if the load is connected to the common or suite distribution (or both)
3. Description of Existing Electrical Distribution System
a. Provide a description or schematic of the existing electrical distribution system including:
i) How the lot is being supplied from the electrical utility.
ii) The interconnection of the main, common, and suite distribution systems.
Section 4 - Additional Electrical Loads
1. Maximum Load Which can be Added Without BC Hydro Approval
a. Refer to the SEPR worksheet for BC Hydro requirements (BC Hydro Electric Tariff Section 7.1).
2. Estimate of Electrical Capacity Needed to Electrify Heating, Cooling, and Ventilation Systems (if applicable)
a. Fill out the table for heating, cooling, ventilation, and DHW systems that could be electrified.
b. Possible methods for calculating the estimated magnitude of electrical capacity are as follows:
i) Convert the BTU/hr rating of the equipment into kW with considerations for COP of equipment and actual gas usage; or
ii) Calculate the estimated heat loads from weather data; or
iii) Any other method determined by the EPR provider.
c. Indicate if there is an opportunity to reduce the demand on the electrical system, for example:
i) Using high efficiency electrical equipment such as heat pumps.
3. Estimate of the Electrical Capacity Needed to Power Anticipated Future Demands
a. Any anticipated future demands noted by the strata corporation.
b. EV Charging - Consider municipal requirements for new builds, as well as the Zero-Emissions Vehicles Act.
c. Cooling - Consider rising temperatures as well as the CleanBC Roadmap to 2030.
d. Other possible future loads as determined by the EPR provider.
Section 5 - Recommendations
1. Electrical Demand Reduction Strategies
a. List possible demand reduction strategies including, but not limited to, the following measures:
i) Changing lighting from incandescent to LED.
ii) Changing from resistive electrical heating to heat pumps.
iii) Building envelope improvements.
iv) Using an EV Energy Management System (EVEMS) for new or existing EV chargers.
v) Solar and/or battery storage.
2. Recommendations for Electrical Upgrades
a. Consider upgrades that would be required to accommodate electrification measures, such as:
i) An electrical service upgrade.
ii) Upgrades within the electrical distribution system.
3. Estimate of Electrical Capacity Made Available
a. Provide high-level estimates, where possible, of the capacity made available from electrical demand reduction strategies listed above. List any assumptions.
b. Provide high-level estimates, where possible, of the capacity made available from electrical upgrades listed above. List any assumptions.
Note on E7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SEPR OR EPR? Reply: Errors and Omissions Insurance Reply: Use of electrical planning report and EPR - use consistently

## SEPR
Electrical Planning Report - Workbook Note: If each strata lot in the strata plan is supplied with electricity by a utility independently from each other strata lot, only Section 1 of this workbook is required for the electrical planning report.
Section 1 - Strata and Provider Details
Date and Property Details
Date EPR created (DD/MM/YYYY) |  |  |  |  | Is each strata lot in the strata plan supplied with electricity independently from each other strata lot? (yes/no)
If yes, include a description of the electrical distribution to support your answer
Building address
Building common name (If Applicable) |  |  |  |  | Strata #
EPR Provider Contact and Qualifications
Company name
Address
Name |  |  |  |  | Qualifications (P.Eng, AScT, Journeyperson)
Relationship with strata corporation
Error and Omission Insurance (if applicable) (Y/N)
If yes, attach a copy at the end of the electrical planning report.
Section 2 - Executive Summary
Introduction
Summary
Section 3 - Electrical System Details
Existing Electrical Service Capacity
Existing electrical service rating (A, % rated)
Existing electrical service switch/breaker rating (A, % rated)
Existing system operating voltage (V, ф)
Current capacity on the service (kW)
Current peak demand on the service (kW)
Current spare capacity on the service (kW)
Current capacity on the house/common distribution (kW)
Current peak demand on the house/common distribution (kW)
Current spare capacity on the house/common distribution (kW)
Current capacity on the residential distribution (kW)
Current peak demand on the residential distribution (kW)
Current spare capacity on the residential distribution (kW)
How was existing peak demand determined? (Ex. BC Hydro kWh data with application of safety factor, calculated by applicable rules of Canadian Electrical Code [must cite rules referenced])
Existing Electrical Demands
List of existing demands on the electrical system including, without limitation, demands from EV charging infrastructure, heating, cooling, ventilation, and lighting systems.
Type |  |  |  |  | Electrical Distribution (common or suite)
Heating
Cooling
Ventilation
DHW
Lighting systems
Major pumps (sump & sanitary)
Elevators
EV charging
Description of Existing Electrical Distribution
Description or Schematic of Electrical Distribution
Section 4 - Additional Electrical Loads
Estimate of Electrical Capacity Needed to Electrify Heating, Cooling, and Ventilation Systems
If applicable, provide an estimate of the electrical capacity that would be needed to power systems, including heating, cooling, and ventilation systems, that are currently powered by a source other than electricity.
An estimate of the electrical capacity needed for any other anticipated future demands on the electrical system, including electrical capacity needed to power (i) heating, cooling, ventilation and other systems that the strata corporation anticipates may be modified or installed in the future, and (ii) EV charging infrastructure that the strata corporation anticipates may be installed in the future;
System | Description | Quantity | Existing Fuel Source (If Applicable) | Existing Output (BTU/hr) |  | COP of Retrofit Equipment at Design Temp | Estimated Magnitude of Electrical Capacity | Capacity Available at Building Level (Y/N/TBD*)
Space Heating
Space Cooling
Ventilation
EV Charging
DHW
Other Equipment
*TBD: Allows for indication that accommodating loads may be subject to ongoing historical load estimations and energy management systems control that may be integrated in the future.
Section 5 - Recommendations
Electrical Demand Reduction Strategies
List steps, if any, that the strata corporation could practicably undertake to reduce the demand on the electrical system and estimated electrical capacity that would be made available from these demand reduction strategies.
Recommendations for Electrical Upgrades
List upgrades or modifications, if any, to the electrical system that the strata corporation could practicably undertake to increase the capacity of the electrical system.
Estimate of Electrical Capacity Made Available
Estimated electrical capacity that would be made available from demand reduction strategies, upgrades or modifications to the electrical system listed above.