| ii. Electrical Planning Report - Workbook Note: If each strata lot in the strata plan is supplied with electricity by a utility independently from each other strata lot, only Section 1 of this workbook is required for the electrical planning report. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Section 1 - Strata and Provider Details |  |  |  |  |  |  |  |  |  |  |  |
| Date and Property Details |  |  |  |  |  |  |  |  |  |  |  |  |
| Date EPR created (DD/MM/YYYY) |  |  |  |  |  |  |  | Is each strata lot in the strata plan supplied with electricity independently from each other strata lot? (yes/no) |  |  |  |
|  |  |  |  |  |  |  |  | If yes, include a description of the electrical distribution to support your answer |  |  |  |
| Building address |  |  |  |  |  |  |  |  |  |  |  |
| Building common name (If Applicable) |  |  |  |  |  |  |  | Strata # |  |  |  |
| EPR Provider Contact and Qualifications |  |  |  |  |  |  |  |  |  |  |  |
| Company name |  |  |  |  |  |  |  |  |  |  |  |  |
| Address |  |  |  |  |  |  |  |  |  |  |  |  |
| Name |  |  |  |  |  |  |  | Qualifications (P.Eng, AScT, Journeyperson) |  |  |  |
| Relationship with strata corporation |  |  |  |  |  |  |  |  |  |  |  |  |
| Error and Omission Insurance (if applicable) (Y/N) |  |  |  |  |  |  |  |  |  |  |  |  |
| If yes, attach a copy at the end of the electrical planning report. |  |  |  |  |  |  |  |  |  |  |  |
| Section 2 - Executive Summary |  |  |  |  |  |  |  |  |  |  |  |
| Introduction |  |  |  |  |  |  |  |  |  |  |  |
| Summary |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 3 - Electrical System Details |  |  |  |  |  |  |  |  |  |  |  |  |
| Existing Electrical Service Capacity |  |  |  |  |  |  |  |  |  |  |  |  |
| Existing electrical service rating (A, % rated) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Existing electrical service switch/breaker rating (A, % rated) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Existing system operating voltage (V, ф) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Current capacity on the service (kW) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Current peak demand on the service (kW) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Current spare capacity on the service (kW) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Current capacity on the house/common distribution (kW) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Current peak demand on the house/common distribution (kW) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Current spare capacity on the house/common distribution (kW) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Current capacity on the residential distribution (kW) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Current peak demand on the residential distribution (kW) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Current spare capacity on the residential distribution (kW) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| How was existing peak demand determined? (Ex. BC Hydro kWh data with application of safety factor, calculated by applicable rules of Canadian Electrical Code [must cite rules referenced]) |  |  |  |  |  |  |  |  |  |  |  |  |
| Existing Electrical Demands |  |  |  |  |  |  |  |  |  |  |  |  |
| List of existing demands on the electrical system including, without limitation, demands from EV charging infrastructure, heating, cooling, ventilation, and lighting systems. |  |  |  |  |  |  |  |  |  |  |  |  |
| Type |  |  |  |  |  |  | Electrical Distribution (common or suite) |  |  |  |  |  |
| Heating |  |  |  |  |  |  |  |  |  |  |  |  |
| Cooling |  |  |  |  |  |  |  |  |  |  |  |  |
| Ventilation |  |  |  |  |  |  |  |  |  |  |  |  |
| DHW |  |  |  |  |  |  |  |  |  |  |  |  |
| Lighting systems |  |  |  |  |  |  |  |  |  |  |  |  |
| Major pumps (sump & sanitary) |  |  |  |  |  |  |  |  |  |  |  |  |
| Elevators |  |  |  |  |  |  |  |  |  |  |  |  |
| EV charging |  |  |  |  |  |  |  |  |  |  |  |  |
| Description of Existing Electrical Distribution |  |  |  |  |  |  |  |  |  |  |  |  |
| Description or Schematic of Electrical Distribution |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 4 - Additional Electrical Loads |  |  |  |  |  |  |  |  |  |  |  |  |
| Estimate of Electrical Capacity Needed to Electrify Heating, Cooling, and Ventilation Systems |  |  |  |  |  |  |  |  |  |  |  |  |
| If applicable, provide an estimate of the electrical capacity that would be needed to power systems, including heating, cooling, and ventilation systems, that are currently powered by a source other than electricity. An estimate of the electrical capacity needed for any other anticipated future demands on the electrical system, including electrical capacity needed to power (i) heating, cooling, ventilation and other systems that the strata corporation anticipates may be modified or installed in the future, and (ii) EV charging infrastructure that the strata corporation anticipates may be installed in the future; |  |  |  |  |  |  |  |  |  |  |  |  |
| System; Description; Quantity; Existing Fuel Source (If Applicable); Existing Output (BTU/hr); COP of Retrofit Equipment at Design Temp; Estimated Magnitude of Electrical Capacity (kW); Capacity Available at Main Service (Y/N/TBD*). Space Heating. Space Cooling. MUA. DHW. EV Charging. Other. |  |
| *TBD: Allows for indication that accommodating loads may be subject to ongoing historical load estimations and energy management systems control that may be integrated in the future. |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 5 - Recommendations Electrical Demand Reduction Strategies |  |  |  |  |  |  |  |  |  |  |  |  |
| List steps, if any, that the strata corporation could practicably undertake to reduce the demand on the electrical system and estimated electrical capacity that would be made available from these demand reduction strategies. |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendations for Electrical Upgrades |  |  |  |  |  |  |  |  |  |  |  |  |
| List upgrades or modifications, if any, to the electrical system that the strata corporation could practicably undertake to increase the capacity of the electrical system. |  |  |  |  |  |  |  |  |  |  |  |  |
| Estimate of Electrical Capacity Made Available |  |  |  |  |  |  |  |  |  |  |  |  |
| Estimated electrical capacity that would be made available from demand reduction strategies, upgrades or modifications to the electrical system listed above. |  |  |  |  |  |  |  |  |  |  |  |  |